## Instructions
Instructions — How to Use This Workbook
1) Open the Inputs_Calcs tab. In the header, enter: Project Name, Units, blended Electricity $/kWh, and (if applicable) Demand $/kW, Fixed $/mo, Billing Demand (kW), Months/Year.
2) Interior Lighting: enter areas (ft²) for each common-space row. LPDs auto-fill from Lookups_References. If space planning isn't final, use the 'MFOther (blended preset)' line as a placeholder, then replace with exact spaces later.
3) Parking Garage: enter garage area and confirm the Parking Garage LPD (defaults to a placeholder). Set hours, days, and a control factor. If the garage is mechanically ventilated, choose Yes and fill the simple fan W/ft², hours, and days.
4) EV Chargers: set Total Parking Spaces and the % EV Charger Spaces on the Parking Garage section; the EV section pulls those values automatically. Adjust kW/port and hours/day as needed.
5) Site Lighting: paste Installed Watts per category from NRCC-LTO. Adjust hours/day and control factor to match expected controls (e.g., photocell, motion bi-level).
6) Pools/Spas (if any): fill pump HP, efficiency, hours/days. Add heater inputs only if present (Electric or Gas).
7) Review the roll-up at the bottom of Inputs_Calcs and the client-facing Report_Client tab. Print or export Report_Client.
8) Lookups_References: holds the LPD table, rate shells, and citations. Update rates (blended $/kWh, demand $/kW, fixed $/mo) as needed and record the source & effective date.

## Inputs_Calcs
Inputs & Calculations — Multifamily Common Areas (Blended Rates)
Project Name | Modera Neptune |  | Units (count) | 359 |  | Electricity Rate ($/kWh) | 0.22 |  | Gas Rate ($/therm) | 1.5 |  | Billing Demand (kW) | 0
[6 empty] | Demand $/kW | 0 |  | Fixed $/mo | 0 |  | Billing Months/Year | 12
[12 empty] | Annual Demand $ | 0
[12 empty] | Annual Fixed $ | 0
DATA COLLECTION — Project Areas, Counts & Assumptions
Areas by Type
Area Type (matches lighting table) | Area (ft²) | Conditioned? (Yes/No) | Ventilated? (Yes/No) | Notes
Corridor Area | 36433 | Yes | Yes
Stairwell | 3779 | No | Yes
Lobby, Main Entry | 3975 | Yes | Yes
Lounge / Club Room | 2611 | Yes | Yes
Exercise / Fitness | 3553 | Yes | Yes
Office Area (> 250 ft²) | 685 | Yes | Yes
Office Area (≤ 250 ft²) | 0 | Yes | Yes
Restrooms (Common) | 439 | Yes | Yes
Laundry (Common) | 0 | Yes | Yes
Electrical/Mechanical/Telephone | 2851 | No | Yes
Storage – Warehouse | 1084 | Yes | Yes
Kitchen / Food Prep | 0 | Yes | Yes
MFOther (blended preset) | 0 | Yes | Yes | Enter blended or non-blended not both
Parking Garage | 182151 | No | Yes
Blended Annual Rates — Electricity & Gas | 0 | Yes | Yes | Not developed yet
Utility | 0 | Yes | Yes
PG&E | 0 | Yes | Yes
PG&E | 0 | Yes | Yes
PG&E | 0 | Yes | Yes
SCE | 0 | Yes | Yes
SCE | 0 | Yes | Yes
SCE | 0 | Yes | Yes
SDG&E | 0 | Yes | Yes
SDG&E | 0 | Yes | Yes
SDG&E | 0 | Yes | Yes
Other/Custom | 0 | Yes | Yes
Parking Garage | 0 | No | Yes
Surface Parking | 0 | No | No
Counts & Equipment
# of Elevators | 4
Total Parking Spaces | 450
% EV Charger Spaces of Total | 10%
Installed L2 Ports (override) | 0
Rated kW per EV Port | 7.2
Avg Use per EV Port (hours/day) | 6
# of Pools/Spas | 2
Site Lighting (NRCC-LTO) — Inputs
Category / Location | Installed Watts | Hours/Day | Days/Year | Control Factor (0–1)
Hardscape / Parking Areas | 0 | 11 | 365 | 0.6
Walkways & Stairways (Exterior) | 0 | 11 | 365 | 0.6
Driveways / Roadways | 0 | 11 | 365 | 0.6
Building Facade | 520 | 6 | 365 | 1
Entrance Canopies & Overhangs | 0 | 11 | 365 | 1
Landscape / Accent | 532.1 | 6 | 365 | 1
Outdoor Dining / Patio (if any) | 0 | 6 | 365 | 1
Parking Garage — Data
Parking Garage Area (ft²) | 182151
Mechanically Ventilated? (Yes/No) | Yes
Vent Fan Power Density (W/ft²) | 0.1
Vent Hours/Day | 12
Vent Days/Year | 365
Pools / Spas — Data
Heat Source (Gas/Electric/Heat Pump) | Gas boiler
Pool Size (ft² surface area) | 465
Pump HP per Pool | 2.5 | [8 empty] | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4
Heater Load Fraction (0–1) | 0.5
Heater Hours/Day | 8
Heater Days/Year | 180
Boiler Efficiency (0–1) | 0.85
HP Pool Heater COP | 4
Pump HP per Pool | 2
Pump Efficiency (0–1) | 0.7
Pump Hours/Day | 12
Pump Days/Year | 365
HVAC — Space Conditioning & Ventilation (Assumptions)
Heating EUI (kWh/ft²·yr) — HP min-eff | 2
Cooling EUI (kWh/ft²·yr) — HP min-eff | 1.5
Ventilation W/ft² (balanced const-speed) | 0.3
Vent Hours/Day (constant) | 24
Vent Days/Year | 365
Vent Hours/Day | 12
Vent Days/Year | 365
Interior Lighting — Calculations (LPD × Area × schedules × factors)
Space Type (fixed) | Area (ft²) | LPD (W/ft²) | Hours/Year | Control Factor (0–1) | Diversity (0–1) | Connected kW | kWh/yr | $/yr
Corridor Area | 36433 | 0.4 | 4380 | 0.8 | 0.9 | 14.5732 | 45958.0435 | 10110.7696
Stairwell | 3779 | 0.6 | 8760 | 0.8 | 1 | 2.2674 | 15889.9392 | 3495.7866
Lobby, Main Entry | 3975 | 0.7 | 4380 | 0.8 | 1 | 2.7825 | 9749.88 | 2144.9736
Lounge / Club Room | 2611 | 0.55 | 3000 | 0.8 | 1 | 1.4361 | 3446.52 | 758.2344
Exercise / Fitness | 3553 | 0.5 | 3500 | 0.8 | 1 | 1.7765 | 4974.2 | 1094.324
Office Area (> 250 ft²) | 685 | 0.6 | 3000 | 0.8 | 1 | 0.411 | 986.4 | 217.008
Office Area (≤ 250 ft²) | 0 | 0.65 | 3000 | 0.8 | 1 | 0 | 0 | 0
Restrooms (Common) | 439 | 0.65 | 4380 | 0.8 | 1 | 0.28535 | 999.8664 | 219.9706
Laundry (Common) | 0 | 0.45 | 3000 | 0.8 | 1 | 0 | 0 | 0
Electrical/Mechanical/Telephone | 2851 | 0.4 | 3000 | 0.8 | 1 | 1.1404 | 2736.96 | 602.1312
Storage – Warehouse | 1084 | 0.4 | 3000 | 0.8 | 1 | 0.4336 | 1040.64 | 228.9408
Kitchen / Food Prep | 0 | 0.95 | 3500 | 0.8 | 1 | 0 | 0 | 0
MFOther (blended preset) | 0 | 0.55 | 3500 | 0.8 | 1 | 0 | 0 | 0
Parking Garage | 182151 | 0.3 | 3000 | 0.8 | 1 | 54.6453 | 131148.72 | 28852.7184
Blended Annual Rates — Electricity & Gas | 0 | 0 | 3000 | 0.8 | 1 | 0 | 0 | 0
Utility | 0 | Class (kW range) | 3000 | 0.8 | 1 | 0 | 0 | 0
PG&E | 0 | Small (≤20 kW) | 3000 | 0.8 | 1 | 0 | 0 | 0
PG&E | 0 | Small (≤20 kW) | 3000 | 0.8 | 1 | 0 | 0 | 0
PG&E | 0 | Small (≤20 kW) | 3000 | 0.8 | 1 | 0 | 0 | 0
SCE | 0 | Small (≤20 kW) | 3000 | 0.8 | 1 | 0 | 0 | 0
SCE | 0 | Small (≤20 kW) | 3000 | 0.8 | 1 | 0 | 0 | 0
SCE | 0 | Small (≤20 kW) | 3000 | 0.8 | 1 | 0 | 0 | 0
SDG&E | 0 | Small (≤20 kW) | 3000 | 0.8 | 1 | 0 | 0 | 0
SDG&E | 0 | Small (≤20 kW) | 3000 | 0.8 | 1 | 0 | 0 | 0
SDG&E | 0 | Small (≤20 kW) | 3000 | 0.8 | 1 | 0 | 0 | 0
Other/Custom | 0 | Any | 3000 | 0.8 | 1 | 0 | 0 | 0
[7 empty] | Interior Lighting kWh/yr — Subtotal | Interior Lighting $/yr — Subtotal
[7 empty] | 216931.1691 | 47724.8572
Elevators
# of Elevators | 4
Assumed kWh per Elevator per Year | 8000
Elevators — Annual kWh | 32000
Elevators — Annual $ | 7040
EV Chargers (Level 2)
Total Parking Spaces | 450
% of Spaces with L2 Ports | 0.1
Installed L2 Ports (override) | 0
Installed L2 Ports (used) | 45
Rated kW per Port | 7.2
Avg Use per Port (hours/day) | 6
EV — kWh per Port per Year | 15768
EV — Annual kWh | 709560
EV — Annual $ | 156103.2
Site Lighting (paste NRCC-LTO installed watts; enter hours & control factor)
Category / Location | Installed Watts | Hours/Day | Days/Year | Control Factor (0–1) | kW | kWh/yr | $/yr
Hardscape / Parking Areas | 0 | 11 | 365 | 0.6 | 0 | 0 | 0
Walkways & Stairways (Exterior) | 0 | 11 | 365 | 0.6 | 0 | 0 | 0
Driveways / Roadways | 0 | 11 | 365 | 0.6 | 0 | 0 | 0
Building Facade | 520 | 6 | 365 | 1 | 0.52 | 1138.8 | 250.536
Entrance Canopies & Overhangs | 0 | 11 | 365 | 1 | 0 | 0 | 0
Landscape / Accent | 532.1 | 6 | 365 | 1 | 0.5321 | 1165.299 | 256.3658
Outdoor Dining / Patio (if any) | 0 | 6 | 365 | 1 | 0 | 0 | 0
[6 empty] | Site Lighting kWh/yr — Subtotal | Site Lighting $/yr — Subtotal
[6 empty] | 2304.099 | 506.9018
Parking Garage
Parking Garage Area (ft²) | 182151
Parking Lighting LPD (W/ft²) | 0.3
Hours/Day | 12
Days/Year | 365
Control Factor (0–1) | 0.6
Parking Lighting — Connected kW | 54.6453
Parking Lighting — Annual kWh | 143607.8484
Parking Lighting — Annual $ | 31593.7266
Mechanically Ventilated? (Yes/No) | Yes
Vent Fan Power Density (W/ft²) | 0.1
Vent Hours/Day | 12
Vent Days/Year | 365
Ventilation — Connected kW | 18.2151
Ventilation — Annual kWh | 79782.138
Ventilation — Annual $ | 17552.0704
Pools / Spas (Revised)
# of Pools/Spas | 2
Pump HP per Pool | 2.5
Pump Efficiency (0–1) | 0.7
Pump Hours/Day | 12
Pump Days/Year | 365
Pump kW per Pool | 2.6643
Pump kWh per Pool per Year | 11669.5714
Pumps — Annual kWh | 23339.1429
Pumps — Annual $ | 5134.6114
Heat Source (Gas/Electric/Heat Pump) | Gas boiler
Pool Size (ft² surface area) | 465
Heater Load Factor (W/ft²) [Lookup] | 10
Heater Hours/Day [Lookup] | 8
Heater Days/Year [Lookup] | 180
Boiler Efficiency (0–1) [Lookup] | 0.85
HP Pool Heater COP [Lookup] | 4
HP Pool Heater COP | 4
Heater Size — kW (normalized from Pool Size) | 4.65
Heater Size — kBtu/h (normalized) | 15.8658
Heater Size — kBtu/h (normalized) | 465
Heater kWh per Pool per Year (Electric/HP) | 0
Heater therms per Pool per Year (Gas) | 268.7853
Heater therms per Pool per Year (Gas) | 1422.9
Heaters — Annual kWh (Electric/HP) | 0
Heaters — Annual therms (Gas) | 537.5706
Heaters — Annual $ (Electric/HP) | 0
Heaters — Annual $ (Gas) | 806.356
HVAC — Space Conditioning & Ventilation (Calculated)
Total Conditioned Area (ft²) | 48780
Total Ventilated Area (ft²) | 237561
Heating — Annual kWh (HP min-eff) | 97560
(removed) Heating — Annual therms (not used) | 0
Heating — Annual $ (electric HP) | 21463.2
(removed) Heating — Annual $ (gas) | 0
Cooling — Annual kWh (HP) | 73170
Cooling — Annual $ | 16097.4
Ventilation — Annual kWh (balanced const-speed) | 145617.48
Ventilation — Annual $ | 32035.8456
Summary (Auto)
Interior Lighting — Annual kWh | 216931.1691
Interior Lighting — Annual $ | 47724.8572
Elevators — Annual kWh | 32000
Elevators — Annual $ | 7040
EV Chargers — Annual kWh | 709560
EV Chargers — Annual $ | 156103.2
Site Lighting — Annual kWh | 2304.099
Site Lighting — Annual $ | 506.9018
Parking Garage — Lighting $ | 31593.7266
Parking Garage — Ventilation $ | 17552.0704
Pools — Pumps (kWh) | 23339.1429
Pools — Pumps (Electric $) | 5134.6114
Pools — Heater (kWh, if electric) | 0
Pools — Heater (therms, if gas) | 537.5706
Pools — Heater (Electric $) | 0
Pools — Heater (Gas $) | 806.356
HVAC — Heating (electric/HP) | 21463.2
HVAC — Heating (gas) — (not used) | 0
HVAC — Cooling (electric) | 16097.4
HVAC — Ventilation (fans) | 32035.8456
TOTAL — Electric $ (all categories + demand + fixed) | 335251.813
TOTAL — Gas $ | 806.356
GRAND TOTAL ($/yr) | 336058.169
Per-Unit Per Month ($/unit·mo) | 78.0079

## Definitions
Definitions — Technical Terms & Inputs
Term | Definition / How Used
LPD (Lighting Power Density, W/ft²) | Watts of installed lighting per square foot. Used with area to compute connected kW: kW = Area × LPD / 1000.
Control Factor (0–1) | Represents average reduction from controls (e.g., occupancy/bi-level). 0.60 means 40% average reduction vs. full power.
Diversity Factor (0–1) | Represents non-simultaneous operation across a group. Commonly 0.90 for corridors; 1.00 otherwise.
Blended Electricity Rate ($/kWh) | Single average energy charge used across all kWh; excludes demand/fixed which are added separately.
Demand Charge ($/kW) | Monthly charge per billing kW; annual demand $ = $/kW × billing kW × months.
Fixed Charge ($/mo) | Monthly customer charge; annual fixed $ = $/mo × months.
Hours/Day; Days/Year | Operating schedule inputs used to derive annual hours.
MFOther (blended preset) | Temporary common-area lighting category with a blended LPD used before exact occupancy definitions are finalized.
Mechanically Ventilated (Parking) | Yes/No toggle. If Yes, ventilation energy is computed from fan W/ft², area, and hours.
Installed Watts (Site Lighting) | Total connected exterior lighting watts by category from NRCC-LTO prescriptive calculations.
EV Charger % of Parking | Percent of total parking spaces equipped with EV charging; used to estimate # of ports or spaces.

## Lookups_References
Lighting Power Densities — Title 24 (2022) Table 140.6-C (Common MF Spaces)
Space Type | LPD (W/ft²) | Notes
Corridor Area | 0.4 | Standard corridors
Stairwell | 0.6 | Common stairwells
Lobby, Main Entry | 0.7 | Entry lobby
Lounge / Club Room | 0.55 | Amenity lounge/club room
Exercise / Fitness | 0.5 | Fitness room/gym
Office Area (> 250 ft²) | 0.6 | Leasing office
Office Area (≤ 250 ft²) | 0.65 | Small office
Restrooms (Common) | 0.65
Laundry (Common) | 0.45
Electrical/Mechanical/Telephone | 0.4
Storage – Warehouse | 0.4
Kitchen / Food Prep | 0.95 | Clubhouse kitchen
MFOther (blended preset) | 0.55 | Use before occupancy definitions are finalized; replace with specific spaces later.
Parking Garage | 0.3 | Placeholder LPD; edit per design / local code interpretation.
Blended Annual Rates — Electricity & Gas
Utility | Class (kW range) | Energy $/kWh | Demand $/kW | Fixed $/mo | Tariff Code | Effective Date | Source / Notes
PG&E | Small (≤20 kW) | 0.34 | 0 | 15 | B-1 (Small General Service TOU) | 2025-08 (planning default) | Planning default; confirm latest PG&E tariff for project.
PG&E | Medium (20–200 kW) | 0.27 | 23 | 150 | E-19 / B-19 (verify) | 2025-08 (planning default) | Planning default; verify actual tariff selection and demand components.
PG&E | Large (>200 kW) | 0.24 | 28 | 300 | E-20 (verify) | 2025-08 (planning default) | Planning default; verify ratchets / transmission demand.
SCE | Small (≤20 kW) | 0.28 | 0 | 16 | TOU-GS-1 | 2025-08 (planning default) | Planning default for SCE GS-1.
SCE | Medium (20–200 kW) | 0.24 | 18 | 100 | TOU-GS-2 | 2025-08 (planning default) | Planning default for SCE GS-2 (demand).
SCE | Large (>200 kW) | 0.22 | 22 | 150 | TOU-GS-3 | 2025-08 (planning default) | Planning default for SCE GS-3 (demand).
SDG&E | Small (≤20 kW) | 0.33 | 0 | 20 | AL-TOU (Small) | 2025-08 (planning default) | Planning default for SDG&E AL-TOU small.
SDG&E | Medium (20–200 kW) | 0.28 | 20 | 120 | AL-TOU (Med) / AL-TOU2 | 2025-08 (planning default) | Planning default for SDG&E medium (demand).
SDG&E | Large (>200 kW) | 0.26 | 24 | 180 | AL-TOU (Large) / AL-TOU2 | 2025-08 (planning default) | Planning default for SDG&E large (demand).
Other/Custom | Any | 0.3 | 0 | 0 | Enter tariff | 2025-08 (placeholder) | Use for non-IOUs or custom blends.
References & Sources (Traceability)
Topic | Reference / Source | Notes (why/how used)
LPD values | CA Title 24, Part 6 (2022) — Table 140.6-C | Used for interior common-area lighting power densities.
Outdoor control schemes | Title 24 §130.2 (Outdoor Lighting Controls) | Default assumptions for hours/control; user can override.
NRCC-LTO | Nonresidential Certificate of Compliance (Outdoor Lighting) | Installed Watts pasted into Site Lighting.
DRE Budget mapping | RE 623 Budget Worksheet (California DRE) | Roll-up to 201 Electricity and 202 Gas for HOA budgets.
Tariffs | PG&E / SCE / SDG&E official rate sheets | Enter blended annual $/kWh, demand $/kW, fixed $/mo.
Pool Defaults | Value
Heater Load Factor (W/ft²) | 10
Heater Hours/Day | 8
Heater Days/Year | 180
Boiler Efficiency (0–1) | 0.85
Heat Pump COP | 4
Pump Efficiency (0–1) | 0.7
Pump Hours/Day | 12
Pump Days/Year | 365
HVAC Defaults | Value
Heating EUI (kWh/ft²·yr) — HP min-eff | 2
Cooling EUI (kWh/ft²·yr) — HP min-eff | 1.5
Ventilation W/ft² (balanced const-speed) | 0.3
Vent Hours/Day (constant) | 24
Vent Days/Year | 365

## Report_Client
Solar Cost Offset Calculation
Project: Modera Neptune Oceanside
Date: 10/28/25 |  | Show therms | Show kBtu | Show Cost | Show Gas
| Yes | Yes | Yes | Yes | Yes
Solar Cost Offset Calculation - provides an estimate of the common area energy loads by applying the overall energy consumption percentage of T24 to the total building footprint. Design Phase Estimate - actual energy consumption will vary based on real-world usage patterns and operational conditions.
Energy Use and Cost by Category
Category | kWh/yr | therms/yr | kBtu/yr | $/yr
EV Chargers (L2) | 709560 | 0 | 2421018.72 | 156103.2
EV Charging — subtotal | 709560 | 0 | 2421018.72 | 156103.2
Lighting — Interior | 216931.1691 | 0 | 740169.149 | 47724.8572
Lighting — Site | 2304.099 | 0 | 7861.5858 | 506.9018
Parking — Lighting | 143607.8484 | 0 | 489989.9787 | 31593.7266
Lighting — subtotal | 362843.1165 | 0 | 1238020.7136 | 79825.4856
HVAC — Heating (HP) | 97560 | 0 | 332874.72 | 21463.2
HVAC — Cooling | 73170 | 0 | 249656.04 | 16097.4
HVAC — Ventilation | 145617.48 | 0 | 496846.8418 | 32035.8456
HVAC — subtotal | 316347.48 | 0 | 1079377.6018 | 69596.4456
Parking Structure — Ventilation | 79782.138 | 0 | 272216.6549 | 17552.0704
Parking (Ventilation) — subtotal | 79782.138 | 0 | 272216.6549 | 17552.0704
Elevators | 32000 | 0 | 109184 | 7040
Elevators — subtotal | 32000 | 0 | 109184 | 7040
Pools — Pumps | 23339.1429 | 0 | 79633.1554 | 5134.6114
Pools — Heater (Electric/HP) | 0 | 0 | 0 | 0
Pools — Heater (Gas) | 0 | 537.5706 | 53757.0635 | 806.356
Pools — subtotal | 23339.1429 | 537.5706 | 133390.219 | 5940.9674
Grand Total | 1523871.8774 | 537.5706 | 5253207.9091 | 336058.169
Reference / Source |  | Notes
CA Title 24, Part 6 (2022) — Table 140.6-C |  | Used for interior common-area lighting power densities.
Title 24 §130.2 (Outdoor Lighting Controls) |  | Default assumptions for hours/control; user can override.
Nonresidential Certificate of Compliance (Outdoor Lighting) |  | Installed Watts pasted into Site Lighting.
RE 623 Budget Worksheet (California DRE) |  | Roll-up to 201 Electricity and 202 Gas for HOA budgets.
PG&E / SCE / SDG&E official rate sheets 2025 |  | Enter blended annual $/kWh, demand $/kW, fixed $/mo.
Assumptions
Electricity Rate ($/kWh) |  | 0.22
Gas Rate ($/therm) |  | 1.5
Rated kW per EV Port |  | 7.2
Avg Use per EV Port (hours/day) |  | 6
Basis of Calculations
Pool Size (ft² surface area) |  | 465
Parking Garage Area (ft²) |  | 182151
Hardscape / Parking Areas |  | 0
# of Elevators |  | 4
Total Parking Spaces |  | 450
% EV Charger Spaces of Total |  | 10%
Total Conditioned Area (ft²) |  | 48780
Unconditioned Ventilated Area |  | 55410