## Instructions
Instructions — How to Use This Workbook
1) Open the Inputs_Calcs tab. In the header, enter: Project Name, Units, blended Electricity $/kWh, and (if applicable) Demand $/kW, Fixed $/mo, Billing Demand (kW), Months/Year.
2) Interior Lighting: enter areas (ft²) for each common-space row. LPDs auto-fill from Lookups_References. If space planning isn't final, use the 'MFOther (blended preset)' line as a placeholder, then replace with exact spaces later.
3) Parking Garage: enter garage area and confirm the Parking Garage LPD (defaults to a placeholder). Set hours, days, and a control factor. If the garage is mechanically ventilated, choose Yes and fill the simple fan W/ft², hours, and days.
4) EV Chargers: set Total Parking Spaces and the % EV Charger Spaces on the Parking Garage section; the EV section pulls those values automatically. Adjust kW/port and hours/day as needed.
5) Site Lighting: paste Installed Watts per category from NRCC-LTO. Adjust hours/day and control factor to match expected controls (e.g., photocell, motion bi-level).
6) Pools/Spas (if any): fill pump HP, efficiency, hours/days. Add heater inputs only if present (Electric or Gas).
7) Review the roll-up at the bottom of Inputs_Calcs and the client-facing Report_Client tab. Print or export Report_Client.
8) Lookups_References: holds the LPD table, rate shells, and citations. Update rates (blended $/kWh, demand $/kW, fixed $/mo) as needed and record the source & effective date.

## Inputs_Calcs
Inputs & Calculations — Multifamily Common Areas (Blended Rates)
Project Name | Ventura & 7th |  | Units (count) | 54 |  | Electricity Rate ($/kWh) | 0.22 |  | Gas Rate ($/therm) | 1.5 |  | Billing Demand (kW) | 0
[6 empty] | Demand $/kW | 0 |  | Fixed $/mo | 0 |  | Billing Months/Year | 12
[12 empty] | Annual Demand $ | 0
[12 empty] | Annual Fixed $ | 0
DATA COLLECTION — Project Areas, Counts & Assumptions
Areas by Type
Area Type (matches lighting table) | Area (ft²) | Conditioned? (Yes/No) | Ventilated? (Yes/No) | Notes
Corridor Area | 7997.98 | No | Yes
Stairwell | 2474.9 | No | Yes
Lobby, Main Entry | 0 | Yes | Yes
Lounge / Club Room | 834.13 | Yes | Yes
Exercise / Fitness | 587.2 | Yes | Yes
Office Area (> 250 ft²) | 937.78 | Yes | Yes
Office Area (≤ 250 ft²) | 0 | Yes | Yes
Restrooms (Common) | 324.86 | Yes | Yes
Laundry (Common) | 610.88 | Yes | Yes
Electrical/Mechanical/Telephone | 3475.66 | No | Yes
Storage – Warehouse | 983.25 | Yes | Yes
Kitchen / Food Prep | 0 | Yes | Yes
MFOther (blended preset) | 0 | Yes | Yes | Enter blended or non-blended not both
Parking Garage | 0 | No | Yes | Enter this below in the Parking Garage inputs
Blended Annual Rates — Electricity & Gas | 0 | Yes | Yes | Not developed yet
Utility | 0 | Yes | Yes
PG&E | 0 | Yes | Yes
PG&E | 0 | Yes | Yes
PG&E | 0 | Yes | Yes
SCE | 0 | Yes | Yes
SCE | 0 | Yes | Yes
SCE | 0 | Yes | Yes
SDG&E | 0 | Yes | Yes
SDG&E | 0 | Yes | Yes
SDG&E | 0 | Yes | Yes
Other/Custom | 0 | Yes | Yes
Parking Garage | 0 | No | Yes
Surface Parking | 0 | No | No
Counts & Equipment
# of Elevators | 1
Total Parking Spaces | 82
% EV Charger Spaces of Total | 10
Installed L2 Ports (override) | 4
Rated kW per EV Port | 7.2
Avg Use per EV Port (hours/day) | 6
# of Pools/Spas | 0
Site Lighting (NRCC-LTO) — Inputs
Category / Location | Installed Watts | Hours/Day | Days/Year | Control Factor (0–1)
Hardscape / Parking Areas | 400 | 13 | 365 | 0.6
Walkways & Stairways (Exterior) | 0 | 11 | 365 | 0.6
Driveways / Roadways | 0 | 11 | 365 | 0.6
Building Facade | 800 | 6 | 365 | 1
Entrance Canopies & Overhangs | 0 | 11 | 365 | 1
Landscape / Accent | 50 | 6 | 365 | 1
Outdoor Dining / Patio (if any) | 0 | 6 | 365 | 1
Parking Garage — Data
Parking Garage Area (ft²) | 0
Mechanically Ventilated? (Yes/No) | No
Vent Fan Power Density (W/ft²) | 0.1
Vent Hours/Day | 12
Vent Days/Year | 365
Pools / Spas — Data
Heat Source (Gas/Electric/Heat Pump) | None
Pool Size (ft² surface area) | 0
Pump HP per Pool | 1 | [8 empty] | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4
Heater Load Fraction (0–1) | 0.5
Heater Hours/Day | 8
Heater Days/Year | 180
Boiler Efficiency (0–1) | 0.85
HP Pool Heater COP | 4
Pump HP per Pool | 2
Pump Efficiency (0–1) | 0.7
Pump Hours/Day | 12
Pump Days/Year | 365
HVAC — Space Conditioning & Ventilation (Assumptions)
Heating EUI (kWh/ft²·yr) — HP min-eff | 2
Cooling EUI (kWh/ft²·yr) — HP min-eff | 1.5
Ventilation W/ft² (balanced const-speed) | 0.3
Vent Hours/Day (constant) | 24
Vent Days/Year | 365
Vent Hours/Day | 12
Vent Days/Year | 365
Interior Lighting — Calculations (LPD × Area × schedules × factors)
Space Type (fixed) | Area (ft²) | LPD (W/ft²) | Hours/Year | Control Factor (0–1) | Diversity (0–1) | Connected kW | kWh/yr | $/yr
Corridor Area | 7997.98 | 0.4 | 4380 | 0.8 | 0.9 | 3.1992 | 10088.9719 | 2219.5738
Stairwell | 2474.9 | 0.6 | 8760 | 0.8 | 1 | 1.4849 | 10406.4595 | 2289.4211
Lobby, Main Entry | 0 | 0.7 | 4380 | 0.8 | 1 | 0 | 0 | 0
Lounge / Club Room | 834.13 | 0.55 | 3000 | 0.8 | 1 | 0.45877 | 1101.0516 | 242.2314
Exercise / Fitness | 587.2 | 0.5 | 3500 | 0.8 | 1 | 0.2936 | 822.08 | 180.8576
Office Area (> 250 ft²) | 937.78 | 0.6 | 3000 | 0.8 | 1 | 0.56267 | 1350.4032 | 297.0887
Office Area (≤ 250 ft²) | 0 | 0.65 | 3000 | 0.8 | 1 | 0 | 0 | 0
Restrooms (Common) | 324.86 | 0.65 | 4380 | 0.8 | 1 | 0.21116 | 739.9011 | 162.7782
Laundry (Common) | 610.88 | 0.45 | 3000 | 0.8 | 1 | 0.2749 | 659.7504 | 145.1451
Electrical/Mechanical/Telephone | 3475.66 | 0.4 | 3000 | 0.8 | 1 | 1.3903 | 3336.6336 | 734.0594
Storage – Warehouse | 983.25 | 0.4 | 3000 | 0.8 | 1 | 0.3933 | 943.92 | 207.6624
Kitchen / Food Prep | 0 | 0.95 | 3500 | 0.8 | 1 | 0 | 0 | 0
MFOther (blended preset) | 0 | 0.55 | 3500 | 0.8 | 1 | 0 | 0 | 0
Parking Garage | 0 | 0.3 | 3000 | 0.8 | 1 | 0 | 0 | 0
Blended Annual Rates — Electricity & Gas | 0 | 0 | 3000 | 0.8 | 1 | 0 | 0 | 0
Utility | 0 | Class (kW range) | 3000 | 0.8 | 1 | 0 | 0 | 0
PG&E | 0 | Small (≤20 kW) | 3000 | 0.8 | 1 | 0 | 0 | 0
PG&E | 0 | Small (≤20 kW) | 3000 | 0.8 | 1 | 0 | 0 | 0
PG&E | 0 | Small (≤20 kW) | 3000 | 0.8 | 1 | 0 | 0 | 0
SCE | 0 | Small (≤20 kW) | 3000 | 0.8 | 1 | 0 | 0 | 0
SCE | 0 | Small (≤20 kW) | 3000 | 0.8 | 1 | 0 | 0 | 0
SCE | 0 | Small (≤20 kW) | 3000 | 0.8 | 1 | 0 | 0 | 0
SDG&E | 0 | Small (≤20 kW) | 3000 | 0.8 | 1 | 0 | 0 | 0
SDG&E | 0 | Small (≤20 kW) | 3000 | 0.8 | 1 | 0 | 0 | 0
SDG&E | 0 | Small (≤20 kW) | 3000 | 0.8 | 1 | 0 | 0 | 0
Other/Custom | 0 | Any | 3000 | 0.8 | 1 | 0 | 0 | 0
[7 empty] | Interior Lighting kWh/yr — Subtotal | Interior Lighting $/yr — Subtotal
[7 empty] | 29449.1713 | 6478.8177
Elevators
# of Elevators | 2
Assumed kWh per Elevator per Year | 8000
Elevators — Annual kWh | 16000
Elevators — Annual $ | 3520
EV Chargers (Level 2)
Total Parking Spaces | 82
% of Spaces with L2 Ports | 10
Installed L2 Ports (override) | 1
Installed L2 Ports (used) | 1
Rated kW per Port | 7.2
Avg Use per Port (hours/day) | 6
EV — kWh per Port per Year | 15768
EV — Annual kWh | 15768
EV — Annual $ | 3468.96
Site Lighting (paste NRCC-LTO installed watts; enter hours & control factor)
Category / Location | Installed Watts | Hours/Day | Days/Year | Control Factor (0–1) | kW | kWh/yr | $/yr
Hardscape / Parking Areas | 400 | 13 | 365 | 0.6 | 0.4 | 1138.8 | 250.536
Walkways & Stairways (Exterior) | 0 | 11 | 365 | 0.6 | 0 | 0 | 0
Driveways / Roadways | 0 | 11 | 365 | 0.6 | 0 | 0 | 0
Building Facade | 800 | 6 | 365 | 1 | 0.8 | 1752 | 385.44
Entrance Canopies & Overhangs | 0 | 11 | 365 | 1 | 0 | 0 | 0
Landscape / Accent | 50 | 6 | 365 | 1 | 0.05 | 109.5 | 24.09
Outdoor Dining / Patio (if any) | 0 | 6 | 365 | 1 | 0 | 0 | 0
[6 empty] | Site Lighting kWh/yr — Subtotal | Site Lighting $/yr — Subtotal
[6 empty] | 3000.3 | 660.066
Parking Garage
Parking Garage Area (ft²) | 0
Parking Lighting LPD (W/ft²) | 0.3
Hours/Day | 12
Days/Year | 365
Control Factor (0–1) | 0.3
Parking Lighting — Connected kW | 0
Parking Lighting — Annual kWh | 0
Parking Lighting — Annual $ | 0
Mechanically Ventilated? (Yes/No) | No
Vent Fan Power Density (W/ft²) | 0.1
Vent Hours/Day | 12
Vent Days/Year | 365
Ventilation — Connected kW | 0
Ventilation — Annual kWh | 0
Ventilation — Annual $ | 0
Pools / Spas (Revised)
# of Pools/Spas | 0
Pump HP per Pool | 1
Pump Efficiency (0–1) | 0.7
Pump Hours/Day | 12
Pump Days/Year | 365
Pump kW per Pool | 1.0657
Pump kWh per Pool per Year | 4667.8286
Pumps — Annual kWh | 0
Pumps — Annual $ | 0
Heat Source (Gas/Electric/Heat Pump) | None
Pool Size (ft² surface area) | 0
Heater Load Factor (W/ft²) [Lookup] | 10
Heater Hours/Day [Lookup] | 8
Heater Days/Year [Lookup] | 180
Boiler Efficiency (0–1) [Lookup] | 0.85
HP Pool Heater COP [Lookup] | 4
HP Pool Heater COP | 4
Heater Size — kW (normalized from Pool Size) | 0
Heater Size — kBtu/h (normalized) | 0
Heater Size — kBtu/h (normalized) | 0
Heater kWh per Pool per Year (Electric/HP) | 0
Heater therms per Pool per Year (Gas) | 0
Heater therms per Pool per Year (Gas) | 0
Heaters — Annual kWh (Electric/HP) | 0
Heaters — Annual therms (Gas) | 0
Heaters — Annual $ (Electric/HP) | 0
Heaters — Annual $ (Gas) | 0
Fire Pumps
Pump HP | 55
Pump Efficiency (0–1) | 0.7
Pump Hours/Day | 1
Pump Days/Year | 1
Pump kW per Pool | 58.6143
Pump kWh per Year | 58.6143
Booster Pumps
Pump HP | 3
Pump Efficiency (0–1) | 0.7
Pump Hours/Day | 24
Pump Days/Year | 365
Pump kW per Pool | 1
Pump kWh per Year | 8760
Recirc
Pump HP | 0.5
Pump Efficiency (0–1) | 0.7
Pump Hours/Day | 24
Pump Days/Year | 365
Pump kW per | 0.53286
Pump kWh per Year | 4667.8286
Water Softener
Pump HP | 1.5
Pump Efficiency (0–1) | 0.7
Pump Hours/Day
Pump Days/Year
Pump kW per
Pump kWh per Year | 0
HVAC — Space Conditioning & Ventilation (Calculated)
Total Conditioned Area (ft²) | 4278.1
Total Ventilated Area (ft²) | 18226.64
Heating — Annual kWh (HP min-eff) | 8556.2
(removed) Heating — Annual therms (not used) | 0
Heating — Annual $ (electric HP) | 1882.364
(removed) Heating — Annual $ (gas) | 0
Cooling — Annual kWh (HP) | 6417.15
Cooling — Annual $ | 1411.773
Ventilation — Annual kWh (balanced const-speed) | 47899.6099
Ventilation — Annual $ | 10537.9142
Summary (Auto)
Interior Lighting — Annual kWh | 29449.1713
Interior Lighting — Annual $ | 6478.8177
Elevators — Annual kWh | 16000
Elevators — Annual $ | 3520
EV Chargers — Annual kWh | 15768
EV Chargers — Annual $ | 3468.96
Site Lighting — Annual kWh | 3000.3
Site Lighting — Annual $ | 660.066
Parking Garage — Lighting $ | 0
Parking Garage — Ventilation $ | 0
Pools — Pumps (kWh) | 0
Pools — Pumps (Electric $) | 0
Pools — Heater (kWh, if electric) | 0
Pools — Heater (therms, if gas) | 0
Pools — Heater (Electric $) | 0
Pools — Heater (Gas $) | 0
HVAC — Heating (electric/HP) | 1882.364
HVAC — Heating (gas) — (not used) | 0
HVAC — Cooling (electric) | 1411.773
HVAC — Ventilation (fans) | 10537.9142
TOTAL — Electric $ (all categories + demand + fixed) | 27959.8949
TOTAL — Gas $ | 0
GRAND TOTAL ($/yr) | 27959.8949
Per-Unit Per Month ($/unit·mo) | 43.148

## Definitions
Definitions — Technical Terms & Inputs
Term | Definition / How Used
LPD (Lighting Power Density, W/ft²) | Watts of installed lighting per square foot. Used with area to compute connected kW: kW = Area × LPD / 1000.
Control Factor (0–1) | Represents average reduction from controls (e.g., occupancy/bi-level). 0.60 means 40% average reduction vs. full power.
Diversity Factor (0–1) | Represents non-simultaneous operation across a group. Commonly 0.90 for corridors; 1.00 otherwise.
Blended Electricity Rate ($/kWh) | Single average energy charge used across all kWh; excludes demand/fixed which are added separately.
Demand Charge ($/kW) | Monthly charge per billing kW; annual demand $ = $/kW × billing kW × months.
Fixed Charge ($/mo) | Monthly customer charge; annual fixed $ = $/mo × months.
Hours/Day; Days/Year | Operating schedule inputs used to derive annual hours.
MFOther (blended preset) | Temporary common-area lighting category with a blended LPD used before exact occupancy definitions are finalized.
Mechanically Ventilated (Parking) | Yes/No toggle. If Yes, ventilation energy is computed from fan W/ft², area, and hours.
Installed Watts (Site Lighting) | Total connected exterior lighting watts by category from NRCC-LTO prescriptive calculations.
EV Charger % of Parking | Percent of total parking spaces equipped with EV charging; used to estimate # of ports or spaces.

## Lookups_References
Lighting Power Densities — Title 24 (2022) Table 140.6-C (Common MF Spaces)
Space Type | LPD (W/ft²) | Notes
Corridor Area | 0.4 | Standard corridors
Stairwell | 0.6 | Common stairwells
Lobby, Main Entry | 0.7 | Entry lobby
Lounge / Club Room | 0.55 | Amenity lounge/club room
Exercise / Fitness | 0.5 | Fitness room/gym
Office Area (> 250 ft²) | 0.6 | Leasing office
Office Area (≤ 250 ft²) | 0.65 | Small office
Restrooms (Common) | 0.65
Laundry (Common) | 0.45
Electrical/Mechanical/Telephone | 0.4
Storage – Warehouse | 0.4
Kitchen / Food Prep | 0.95 | Clubhouse kitchen
MFOther (blended preset) | 0.55 | Use before occupancy definitions are finalized; replace with specific spaces later.
Parking Garage | 0.3 | Placeholder LPD; edit per design / local code interpretation.
Blended Annual Rates — Electricity & Gas
Utility | Class (kW range) | Energy $/kWh | Demand $/kW | Fixed $/mo | Tariff Code | Effective Date | Source / Notes
PG&E | Small (≤20 kW) | 0.34 | 0 | 15 | B-1 (Small General Service TOU) | 2025-08 (planning default) | Planning default; confirm latest PG&E tariff for project.
PG&E | Medium (20–200 kW) | 0.27 | 23 | 150 | E-19 / B-19 (verify) | 2025-08 (planning default) | Planning default; verify actual tariff selection and demand components.
PG&E | Large (>200 kW) | 0.24 | 28 | 300 | E-20 (verify) | 2025-08 (planning default) | Planning default; verify ratchets / transmission demand.
SCE | Small (≤20 kW) | 0.28 | 0 | 16 | TOU-GS-1 | 2025-08 (planning default) | Planning default for SCE GS-1.
SCE | Medium (20–200 kW) | 0.24 | 18 | 100 | TOU-GS-2 | 2025-08 (planning default) | Planning default for SCE GS-2 (demand).
SCE | Large (>200 kW) | 0.22 | 22 | 150 | TOU-GS-3 | 2025-08 (planning default) | Planning default for SCE GS-3 (demand).
SDG&E | Small (≤20 kW) | 0.33 | 0 | 20 | AL-TOU (Small) | 2025-08 (planning default) | Planning default for SDG&E AL-TOU small.
SDG&E | Medium (20–200 kW) | 0.28 | 20 | 120 | AL-TOU (Med) / AL-TOU2 | 2025-08 (planning default) | Planning default for SDG&E medium (demand).
SDG&E | Large (>200 kW) | 0.26 | 24 | 180 | AL-TOU (Large) / AL-TOU2 | 2025-08 (planning default) | Planning default for SDG&E large (demand).
Other/Custom | Any | 0.3 | 0 | 0 | Enter tariff | 2025-08 (placeholder) | Use for non-IOUs or custom blends.
References & Sources (Traceability)
Topic | Reference / Source | Notes (why/how used)
LPD values | CA Title 24, Part 6 (2022) — Table 140.6-C | Used for interior common-area lighting power densities.
Outdoor control schemes | Title 24 §130.2 (Outdoor Lighting Controls) | Default assumptions for hours/control; user can override.
NRCC-LTO | Nonresidential Certificate of Compliance (Outdoor Lighting) | Installed Watts pasted into Site Lighting.
DRE Budget mapping | RE 623 Budget Worksheet (California DRE) | Roll-up to 201 Electricity and 202 Gas for HOA budgets.
Tariffs | PG&E / SCE / SDG&E official rate sheets | Enter blended annual $/kWh, demand $/kW, fixed $/mo.
Pool Defaults | Value
Heater Load Factor (W/ft²) | 10
Heater Hours/Day | 8
Heater Days/Year | 180
Boiler Efficiency (0–1) | 0.85
Heat Pump COP | 4
Pump Efficiency (0–1) | 0.7
Pump Hours/Day | 12
Pump Days/Year | 365
HVAC Defaults | Value
Heating EUI (kWh/ft²·yr) — HP min-eff | 2
Cooling EUI (kWh/ft²·yr) — HP min-eff | 1.5
Ventilation W/ft² (balanced const-speed) | 0.3
Vent Hours/Day (constant) | 24
Vent Days/Year | 365

## Report_Client
Solar Cost Offset Calculation
Project: 9th and Linden
Date: 9/19/2025 |  | Show therms | Show kBtu | Show Cost | Show Gas
| Yes | Yes | Yes | Yes | Yes
Solar Cost Offset Calculation - provides an estimate of the common area energy loads by applying the overall energy consumption percentage of T24 to the total building footprint. Design Phase Estimate - actual energy consumption will vary based on real-world usage patterns and operational conditions.
Energy Use and Cost by Category
Category | kWh/yr | therms/yr | kBtu/yr | $/yr
EV Chargers (L2) | 15768 | 0 | 53800.416 | 3468.96
EV Charging — subtotal | 15768 | 0 | 53800.416 | 3468.96
Lighting — Site | 3000.3 | 0 | 10237.0236 | 660.066
Parking — Lighting | 0 | 0 | 0 | 0
Exterior Lighting — subtotal | 32449.4713 | 0 | 110717.5962 | 7138.8837
Lighting — Interior | 29449.1713 | 0 | 100480.5726 | 6478.8177
HVAC — Heating (HP) | 8556.2 | 0 | 29193.7544 | 1882.364
HVAC — Cooling | 6417.15 | 0 | 21895.3158 | 1411.773
HVAC — Ventilation | 47899.6099 | 0 | 163433.469 | 10537.9142
DHW * | 5356
Modeled Energy Use | 62872.9599 | 0 | 214522.5392 | 13832.0512
Parking — Ventilation | 0 | 0 | 0 | 0
Parking (Ventilation) — subtotal | 0 | 0 | 0 | 0
Elevators | 16000 | 0 | 54592 | 3520
Elevators — subtotal | 16000 | 0 | 54592 | 3520
Pools — Pumps | 0 | 0 | 0 | 0
Pools — Heater (Electric/HP) | 0 | 0 | 0 | 0
Pools — Heater (Gas) | 0 | 0 | 0 | 0
Pools — subtotal | 0 | 0 | 0 | 0
Extra HPWH load | 0
Fire Pump | 58.6143
Booster Pumps | 8760
Recirc Pumps | 4667.8286
Water Softener | 0
Elevator Shaft RTU | 0
Starewell Freeze Protection | 0
Grand Total | 140576.8741 | 0 | 433632.5515 | 27959.8949
Without EV | 124808.8741
Total (wth modeled) | 564584
Total (No EV) | 548915.8741
Reference / Source |  | Notes
CA Title 24, Part 6 (2022) — Table 140.6-C |  | Used for interior common-area lighting power densities.
Title 24 §130.2 (Outdoor Lighting Controls) |  | Default assumptions for hours/control; user can override.
Nonresidential Certificate of Compliance (Outdoor Lighting) |  | Installed Watts pasted into Site Lighting.
RE 623 Budget Worksheet (California DRE) |  | Roll-up to 201 Electricity and 202 Gas for HOA budgets.
PG&E / SCE / SDG&E official rate sheets 2025 |  | Enter blended annual $/kWh, demand $/kW, fixed $/mo.
Assumptions
Electricity Rate ($/kWh) |  | 0.22
Gas Rate ($/therm) |  | 1.5
Rated kW per EV Port |  | 7.2
Avg Use per EV Port (hours/day) |  | 6
Basis of Calculations
Pool Size (ft² surface area) |  | 0
Parking Garage Area (ft²) |  | 0
Hardscape / Parking Areas |  | 400
# of Elevators |  | 1
Total Parking Spaces |  | 82
% EV Charger Spaces of Total |  | 10
Total Conditioned Area (ft²) |  | 4278.1
Unconditioned Ventilated Area |  | 18226.64