## NR_Envelope_Roofs
Title 24-2022 Prescriptive Requirements - Nonresidential Building Envelope
ROOFS / CEILINGS
Component | Type | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
Metal Buildings | Maximum U-factor | 0.041 | 0.041 | 0.041 | 0.041 | 0.041 | 0.041 | 0.041 | 0.041 | 0.041 | 0.041 | 0.041 | 0.041 | 0.041 | 0.041 | 0.041 | 0.041
Nonmetal Buildings | Maximum U-factor | 0.034 | 0.034 | 0.034 | 0.034 | 0.034 | 0.034 | 0.034 | 0.034 | 0.034 | 0.034 | 0.034 | 0.034 | 0.034 | 0.034 | 0.034 | 0.034
Roofing Products | Type
Low-Sloped | Min Aged Solar Reflectance | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.8 | 0.63 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.63
Low-Sloped | Min Thermal Emittance | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
Steep-Sloped | Min Aged Solar Reflectance | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.2 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.2
Steep-Sloped | Min Thermal Emittance | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75

## NR_Envelope_Walls
Title 24-2022 Prescriptive Requirements - Nonresidential Building Envelope
WALLS
Component | Type | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
Wood Frame | Maximum U-factor | 0.071 | 0.071 | 0.071 | 0.071 | 0.071 | 0.071 | 0.071 | 0.071 | 0.071 | 0.071 | 0.071 | 0.071 | 0.071 | 0.071 | 0.071 | 0.071
Metal Frame | Maximum U-factor | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084
Metal Building | Maximum U-factor | 0.113 | 0.113 | 0.113 | 0.113 | 0.113 | 0.113 | 0.113 | 0.113 | 0.113 | 0.113 | 0.113 | 0.113 | 0.113 | 0.113 | 0.113 | 0.113
Mass (HC≥7.0) | Maximum U-factor | 0.151 | 0.151 | 0.151 | 0.151 | 0.151 | 0.151 | 0.151 | 0.151 | 0.151 | 0.151 | 0.151 | 0.151 | 0.151 | 0.151 | 0.151 | 0.151

## NR_Envelope_Fenestration
Title 24-2022 Prescriptive Requirements - Nonresidential Building Envelope
FENESTRATION (WINDOWS, GLAZED DOORS, SKYLIGHTS)
Component | Type | Metric | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
Fixed Window |  | Max U-factor | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
Fixed Window |  | Max RSHGC | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Fixed Window |  | Min VT | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
Curtainwall/Storefront |  | Max U-factor | 0.38 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.38 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41
Curtainwall/Storefront |  | Max RSHGC | 0.25 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.25 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
Curtainwall/Storefront |  | Min VT | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46
Operable Window |  | Max U-factor | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46
Operable Window |  | Max RSHGC | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22
Operable Window |  | Min VT | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32
Glazed Doors | Site-Built/Factory | Max U-factor | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
Glazed Doors | Site-Built/Factory | Max RSHGC | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23
Glazed Doors | Site-Built/Factory | Min VT | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17
Skylights | Glass, Curb Mounted | Max U-factor | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58
Skylights | Glass, Curb Mounted | Max SHGC | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Skylights | Glass, Deck Mounted | Max U-factor | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46
Skylights | Glass, Deck Mounted | Max SHGC | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Skylights | Plastic, Curb Mounted | Max U-factor | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
Window-to-Wall Ratio |  | Maximum % | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40

## NR_Envelope_Doors
Title 24-2022 Prescriptive Requirements - Nonresidential Building Envelope
EXTERIOR DOORS
Door Type | Metric | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
Non-Swinging | Max U-factor | 0.5 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 0.5
Swinging | Max U-factor | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7

## HVAC_Heat_Pumps
Title 24-2022 Mandatory Requirements - Space-Conditioning Equipment
HEAT PUMPS - MINIMUM EFFICIENCY REQUIREMENTS
Equipment Type | Size Category | Rating Condition | Minimum Efficiency | Test Procedure
Air Cooled (Cooling) | ≥65,000 Btu/h and <135,000 Btu/h |  | 11.0 EER / 14.1 IEER | AHRI 340/360
Air Cooled (Cooling) | ≥135,000 Btu/h and <240,000 Btu/h |  | 10.6 EER / 13.5 IEER | AHRI 340/360
Air Cooled (Cooling) | ≥240,000 Btu/h |  | 9.5 EER / 12.5 IEER | AHRI 340/360
Air Cooled (Heating) | ≥65,000 and <135,000 Btu/h | 47°F db/43°F wb | 3.4 COP | AHRI 340/360
Air Cooled (Heating) | ≥65,000 and <135,000 Btu/h | 17°F db/15°F wb | 2.25 COP | AHRI 340/360
Air Cooled (Heating) | ≥135,000 and <240,000 Btu/h | 47°F db/43°F wb | 3.3 COP | AHRI 340/360
Air Cooled (Heating) | ≥240,000 and <760,000 Btu/h | 47°F db/43°F wb | 3.2 COP | AHRI 340/360
Water Source (Cooling) | ≥65,000 and <135,000 Btu/h | 86°F entering water | 13.0 EER | ISO-13256-1
Groundwater Source (Cooling) | <135,000 Btu/h | 59°F entering water | 18.0 EER | ISO-13256-1
Ground Source (Cooling) | <135,000 Btu/h | 77°F entering water | 14.1 EER | ISO-13256-1

## HVAC_VRF_Systems
Title 24-2022 Mandatory Requirements - Space-Conditioning Equipment
VARIABLE REFRIGERANT FLOW (VRF) - MINIMUM EFFICIENCY REQUIREMENTS
Equipment Type | Size Category | Rating Condition | Minimum Efficiency | Test Procedure
VRF Air Cooled (Cooling) | <65,000 Btu/h |  | 13.0 SEER | AHRI 1230
VRF Air Cooled (Cooling) | ≥65,000 and <135,000 Btu/h |  | 10.3 EER | AHRI 1230
VRF Air Cooled (Cooling) | ≥135,000 and <240,000 Btu/h |  | 9.9 EER | AHRI 1230
VRF Air Cooled (Cooling) | ≥240,000 Btu/h |  | 9.1 EER | AHRI 1230
VRF Air Cooled (Heating) | <65,000 Btu/h |  | 7.7 HSPF | AHRI 1230
VRF Air Cooled (Heating) | ≥65,000 and <135,000 Btu/h | 47°F db/43°F wb | 3.3 COP | AHRI 1230
VRF Air Cooled (Heating) | ≥65,000 and <135,000 Btu/h | 17°F db/15°F wb | 2.25 COP | AHRI 1230
VRF Air Cooled (Heating) | ≥135,000 Btu/h | 47°F db/43°F wb | 3.2 COP | AHRI 1230
VRF Water Source (Cooling) | <65,000 Btu/h | 86°F entering water | 12.0 EER | AHRI 1230
VRF Water Source (Cooling) | ≥65,000 and <135,000 Btu/h | 86°F entering water | 12.0 EER | AHRI 1230
VRF Groundwater (Cooling) | <135,000 Btu/h | 59°F entering water | 16.2 EER | AHRI 1230

## Lighting_NR_Complete_Bldg
Title 24-2022 Prescriptive Requirements - Indoor Lighting
COMPLETE BUILDING METHOD - LIGHTING POWER DENSITY
Building Type | Allowed LPD (W/ft²)
Assembly Building | 0.65
Bank or Financial Institution | 0.65
Grocery Store | 0.9
Gymnasium | 0.6
Healthcare Facility | 0.9
Industrial/Manufacturing | 0.6
Library | 0.7
Motion Picture Theater | 0.6
Museum | 0.65
Office Building | 0.6
Parking Garage | 0.13
Performing Arts Theater | 0.75
Religious Facility | 0.7
Restaurant | 0.65
Retail Store | 0.9
School | 0.6
Sports Arena | 0.75
All Other Buildings | 0.4

## Lighting_NR_Area_Category
Title 24-2022 Prescriptive Requirements - Indoor Lighting
AREA CATEGORY METHOD - LIGHTING POWER DENSITY (Selected Common Areas)
Primary Function Area | General Lighting LPD (W/ft²) | Additional Allowance Type | Additional LPD (W/ft²)
Corridor | 0.7 | Decorative/Display | 0.3
Dining | 0.8 | Decorative/Display | 0.3
Lobby, Main Entry | 0.85 | Decorative/Display | 0.3
Lounge/Waiting Area | 0.8 | Decorative/Display | 0.3
Restroom | 1 | Decorative/Display | 0.2
Stairwell | 0.8 | Decorative/Display | 0.2
Office Area > 250 SF | 0.6 | Decorative/Display | 0.2
Office Area ≤ 250 SF | 0.65 | Decorative/Display | 0.2
Conference/Meeting | 0.75 | Decorative/Display | 0.2
Copy Room | 0.5
Classroom | 0.7 | Specialized Task | 0.4
Gym/Exercise Center | 0.5
Library Reading Area | 0.8 | Decorative/Display | 0.25
Library Stacks | 1
Retail Merchandise Sales | 0.95 | Decorative | 0.35
Retail Merchandise Sales | 0.95 | Wall Display (≤10'6") | 9.5 W/ft
Grocery Sales | 1 | Decorative | 0.35
Grocery Sales | 1 | Wall Display (≤10'6") | 6.6 W/ft
Parking Garage - Parking Zone | 0.1
Parking Garage - Daylight Adapt | 1

## MF_Envelope_Summary
Title 24-2022 Prescriptive Requirements - Multifamily Buildings
ENVELOPE REQUIREMENTS (SELECTED CLIMATE ZONES)
Component | Type | Metric | CZ1 | CZ3 | CZ6 | CZ9 | CZ12 | CZ16
Roof/Ceiling | Wood Frame | Max U-factor | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024
Exterior Walls | Wood Frame | Max U-factor | 0.065 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048
Exterior Walls | Steel Frame | Max U-factor | 0.084 | 0.071 | 0.071 | 0.071 | 0.071 | 0.071
Fenestration | All Other Windows | Max U-factor | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Fenestration | All Other Windows | Max RSHGC | NR | 0.23 | 0.23 | 0.23 | 0.23 | NR
Fenestration | Curtainwall/Storefront | Max U-factor | 0.38 | 0.41 | 0.41 | 0.41 | 0.41 | 0.38
Fenestration |  | Max WWR | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Entry Doors | Dwelling Unit | Max U-factor | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Entry Doors | Common - Swinging | Max U-factor | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Entry Doors | Common - Non-Swing | Max U-factor | 0.5 | 1.45 | 1.45 | 1.45 | 1.45 | 0.5

## Climate_Zones_Info
California Title 24 Climate Zones
Climate Zone | Representative City | General Characteristics
1 | Arcata | Cool coastal - Heating dominated
2 | Santa Rosa | Moderate coastal - Heating dominated
3 | Oakland | Bay Area coastal - Heating dominated
4 | San Jose-Reid | Bay Area - Moderate heating/cooling
5 | Santa Maria | Central coast - Moderate heating
6 | Los Angeles | South coastal - Moderate conditions
7 | San Diego | San Diego coastal - Mild year-round
8 | El Toro | Inland valleys - Moderate heating/cooling
9 | Burbank-Glendale | Inland valleys - Cooling dominated
10 | Riverside | Desert transition - Hot summers
11 | Red Bluff | North central valley - Hot summers
12 | Sacramento | Central valley - Hot dry summers
13 | Fresno | South central valley - Very hot summers
14 | China Lake | High desert - Hot dry, cold winters
15 | Palm Springs-Blythe | Low desert - Very hot summers
16 | Mt. Shasta | Mountain - Cold winters, moderate summers

## Notes_References
Title 24-2022 Prescriptive Requirements
IMPORTANT NOTES AND REFERENCES
KEY ABBREVIATIONS
U-factor | Overall heat transfer coefficient (Btu/h·ft²·°F) - Lower is better
SHGC | Solar Heat Gain Coefficient - Lower blocks more heat
RSHGC | Relative Solar Heat Gain Coefficient (accounts for external shading)
VT | Visible Transmittance - Higher allows more daylight
WWR | Window-to-Wall Ratio
LPD | Lighting Power Density (Watts per square foot)
EER | Energy Efficiency Ratio (Btu/h per Watt)
SEER | Seasonal Energy Efficiency Ratio
IEER | Integrated Energy Efficiency Ratio
COP | Coefficient of Performance (unitless)
HSPF | Heating Seasonal Performance Factor
IMPORTANT COMPLIANCE NOTES
1. Prescriptive vs Performance | Buildings can comply either prescriptively (meet all requirements) or via performance approach (energy modeling)
2. Mandatory Requirements | Some requirements are mandatory regardless of compliance method
3. Climate Zone Specific | Requirements vary by California climate zone (1-16)
4. Updated Standards | This workbook reflects 2022 standards; verify current code year
5. Trade-offs | Some methods allow trade-offs between components
REFERENCES
Title 24, Part 6 | California Energy Code - Building Energy Efficiency Standards
Document | CEC-400-2022-010-CMF (Code of Regulations)
Effective Date | January 1, 2023
Website | www.energy.ca.gov/title24
BASELINE MODELING NOTES
For Energy Models | These prescriptive values establish minimum baselines
Envelope Assemblies | Use overall U-factors, not just insulation R-values
HVAC Systems | Baseline equipment efficiencies shown are minimums
Lighting | LPD values are maximum allowances for baseline
Climate Data | Use appropriate TMY3 or CTZ weather files