## NR_Envelope_Roofs
Title 24-2025 Prescriptive Requirements - Nonresidential Building Envelope
ROOFS / CEILINGS
Component | Type | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
Metal Buildings | Maximum U-factor | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038
Wood Framed & Other | Maximum U-factor | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.047 | 0.047 | 0.047 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
Roofing Products | Type
Low-Sloped | Min Aged Solar Reflectance | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63
Low-Sloped | Min Thermal Emittance | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
Steep-Sloped | Min Aged Solar Reflectance | 0.2 | 0.25 | 0.2 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Steep-Sloped | Min Thermal Emittance | 0.75 | 0.8 | 0.75 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
2025 UPDATES: | Metal building roofs improved from 0.041 to 0.038; Some wood framed changed to 0.047 in CZ 6-8

## NR_Envelope_Walls
Title 24-2025 Prescriptive Requirements - Nonresidential Building Envelope
WALLS
Component | Type | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
Wood Frame & Other | Maximum U-factor | 0.078 | 0.053 | 0.102 | 0.053 | 0.095 | 0.102 | 0.102 | 0.095 | 0.053 | 0.053 | 0.042 | 0.053 | 0.053 | 0.053 | 0.038 | 0.053
Metal Frame | Maximum U-factor | 0.06 | 0.055 | 0.071 | 0.055 | 0.055 | 0.06 | 0.06 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055
Metal Building | Maximum U-factor | 0.098 | 0.053 | 0.098 | 0.053 | 0.053 | 0.098 | 0.098 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.05 | 0.053
Mass - Light (HC≥7.0) | Maximum U-factor | 0.17 | 0.138 | 0.227 | 0.196 | 0.364 | 0.364 | 0.364 | 0.364 | 0.364 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138
Mass - Heavy (HC≥15.0) | Maximum U-factor | 0.211 | 0.65 | 0.65 | 0.65 | 0.65 | 0.69 | 0.69 | 0.69 | 0.69 | 0.65 | 0.16 | 0.211 | 0.184 | 0.16 | 0.16 | 0.153
2025 UPDATES: | Significant improvements across multiple wall types and climate zones compared to 2022

## NR_Envelope_Fenestration
Title 24-2025 Prescriptive Requirements - Nonresidential Building Envelope
FENESTRATION (WINDOWS, GLAZED DOORS, SKYLIGHTS)
Component | Type | Metric | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
Fixed Window |  | Max U-factor | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
Fixed Window |  | Max RSHGC | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Fixed Window |  | Min VT | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
Curtainwall/Storefront |  | Max U-factor | 0.38 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.38 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41
Curtainwall/Storefront |  | Max RSHGC | 0.25 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.25 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
Curtainwall/Storefront |  | Min VT | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46
Operable Window |  | Max U-factor | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46
Operable Window |  | Max RSHGC | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22
Operable Window |  | Min VT | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32
Glazed Doors | Site-Built/Factory | Max U-factor | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
Glazed Doors | Site-Built/Factory | Max RSHGC | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23
Glazed Doors | Site-Built/Factory | Min VT | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17
Skylights | Glass, Curb Mounted | Max U-factor | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58
Skylights | Glass, Curb Mounted | Max SHGC | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Skylights | Glass, Deck Mounted | Max U-factor | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46
Skylights | Glass, Deck Mounted | Max SHGC | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Skylights | Plastic, Curb Mounted | Max U-factor | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
Window-to-Wall Ratio |  | Maximum % | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
2025 UPDATES: | Fenestration requirements remain largely unchanged from 2022

## NR_Envelope_Doors
Title 24-2025 Prescriptive Requirements - Nonresidential Building Envelope
EXTERIOR DOORS
Door Type | Metric | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
Non-Swinging | Max U-factor | 0.5 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 0.5
Swinging | Max U-factor | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7

## HVAC_Heat_Pumps
Title 24-2025 Mandatory Requirements - Space-Conditioning Equipment
HEAT PUMPS - MINIMUM EFFICIENCY REQUIREMENTS
Equipment Type | Size Category | Rating Condition | Minimum Efficiency | Test Procedure
Air Cooled (Cooling) | ≥65,000 Btu/h and <135,000 Btu/h |  | 11.0 EER / Federal Min IEER | AHRI 340/360
Air Cooled (Cooling) | ≥135,000 Btu/h and <240,000 Btu/h |  | 10.6 EER / Federal Min IEER | AHRI 340/360
Air Cooled (Cooling) | ≥240,000 Btu/h |  | 9.5 EER / Federal Min IEER | AHRI 340/360
Air Cooled (Heating) | ≥65,000 and <135,000 Btu/h | 47°F db/43°F wb | Federal Minimum COP | AHRI 340/360
Air Cooled (Heating) | ≥65,000 and <135,000 Btu/h | 17°F db/15°F wb | 2.25 COP | AHRI 340/360
Air Cooled (Heating) | ≥135,000 and <240,000 Btu/h | 47°F db/43°F wb | Federal Minimum COP | AHRI 340/360
Air Cooled (Heating) | ≥240,000 and <760,000 Btu/h | 47°F db/43°F wb | Federal Minimum COP | AHRI 340/360
Air Cooled (Heating) | ≥135,000 Btu/h | 17°F db/15°F wb | 2.05 COP | AHRI 340/360
Water Source (Cooling) | ≥65,000 and <135,000 Btu/h | 86°F entering water | Federal Minimum EER | ISO-13256-1
Groundwater Source (Cooling) | <135,000 Btu/h | 59°F entering water | 18.0 EER | ISO-13256-1
Ground Source (Cooling) | <135,000 Btu/h | 77°F entering water | 14.1 EER | ISO-13256-1
2025 UPDATES: | Many efficiencies now reference "Federal Minimum" values which update automatically with federal standards

## HVAC_VRF_Systems
Title 24-2025 Mandatory Requirements - Space-Conditioning Equipment
VARIABLE REFRIGERANT FLOW (VRF) - MINIMUM EFFICIENCY REQUIREMENTS
Equipment Type | Size Category | Rating Condition | Minimum Efficiency | Test Procedure | Notes
VRF Air Cooled (Cooling) | <65,000 Btu/h |  | 13.0 SEER (Before 1/1/2023) | AHRI 1230 | SEER2 on/after 1/1/2023
VRF Air Cooled (Cooling) | <65,000 Btu/h |  | Federal Min SEER2 (On/after 1/1/2023) | AHRI 210/240
VRF Air Cooled (Cooling) | ≥65,000 and <135,000 Btu/h |  | 10.3 EER / Federal Min IEER | AHRI 1230
VRF Air Cooled (Cooling) | ≥135,000 and <240,000 Btu/h |  | 9.9 EER / Federal Min IEER | AHRI 1230
VRF Air Cooled (Cooling) | ≥240,000 Btu/h |  | 9.1 EER / Federal Min IEER | AHRI 1230
VRF Air Cooled (Heating) | <65,000 Btu/h |  | 7.7 HSPF (Before 1/1/2025) | AHRI 1230 | HSPF2 on/after 1/1/2025
VRF Air Cooled (Heating) | <65,000 Btu/h |  | 7.5 HSPF2 (On/after 1/1/2025) | AHRI 210/240
VRF Air Cooled (Heating) | ≥65,000 and <135,000 Btu/h | 47°F db/43°F wb | Federal Minimum COP | AHRI 1230
VRF Air Cooled (Heating) | ≥65,000 and <135,000 Btu/h | 17°F db/15°F wb | 2.25 COP | AHRI 1230
VRF Air Cooled (Heating) | ≥135,000 Btu/h | 47°F db/43°F wb | Federal Minimum COP | AHRI 1230
VRF Air Cooled (Heating) | ≥135,000 Btu/h | 17°F db/15°F wb | 2.05 COP | AHRI 1230
VRF Water Source (Cooling) | <65,000 Btu/h | 86°F entering water | 12.0 EER / Federal Min IEER | AHRI 1230
VRF Water Source (Cooling) | ≥65,000 and <135,000 Btu/h | 86°F entering water | 12.0 EER / Federal Min IEER | AHRI 1230
VRF Water Source (Cooling) | ≥135,000 and <240,000 Btu/h | 86°F entering water | 10.0 EER / Federal Min IEER | AHRI 1230
VRF Groundwater (Cooling) | <135,000 Btu/h | 59°F entering water | 16.2 EER | AHRI 1230
VRF Ground Source (Cooling) | <135,000 Btu/h | 77°F entering water | 13.4 EER | AHRI 1230
VRF Groundwater (Heating) | <135,000 Btu/h | 50°F entering water | 3.6 COP | AHRI 1230
VRF Ground Source (Heating) | <135,000 Btu/h | 32°F entering water | 3.1 COP | AHRI 1230
2025 UPDATES: | Transition to SEER2/HSPF2 ratings; Many values now reference Federal Minimums

## Lighting_NR_Complete_Bldg
Title 24-2025 Prescriptive Requirements - Indoor Lighting
COMPLETE BUILDING METHOD - LIGHTING POWER DENSITY
Building Type | Allowed LPD (W/ft²)
Assembly Building | 0.65
Bank or Financial Institution | 0.65
Grocery Store | 0.9
Gymnasium | 0.6
Healthcare Facility | 0.9
Industrial/Manufacturing | 0.6
Library | 0.7
Motion Picture Theater | 0.6
Museum | 0.65
Office Building | 0.6
Parking Garage | 0.13
Performing Arts Theater | 0.75
Religious Facility | 0.7
Restaurant | 0.65
Retail Store | 0.9
School | 0.6
Sports Arena | 0.75
All Other Buildings | 0.4
2025 UPDATES: | Complete Building Method LPDs remain unchanged from 2022

## Lighting_NR_Area_Category
Title 24-2025 Prescriptive Requirements - Indoor Lighting
AREA CATEGORY METHOD - LIGHTING POWER DENSITY (Selected Common Areas)
Primary Function Area | General Lighting LPD (W/ft²) | Additional Allowance Type | Additional LPD (W/ft²)
Corridor | 0.4 | Decorative/Display | 0.25
Dining - Bar/Lounge/Fine | 0.45 | Decorative | 0.35
Dining - Cafeteria/Fast Food | 0.45 | Display/Decorative | 0.25
Dining - Family/Leisure | 0.4 | Display/Decorative | 0.25
Lobby, Main Entry | 0.7 | Display | 0.25
Lounge/Waiting/Breakroom | 0.55 | Display/Decorative | 0.25
Restroom | 0.65 | Decorative/Display | 0.35
Stairwell | 0.6 | Decorative/Display | 0.35
Office Area > 250 SF | 0.6 | Decorative/Display | 0.2
Office Area ≤ 250 SF | 0.65 | Decorative/Display | 0.2
Conference/Meeting/Multipurpose | 0.75 | Decorative/Display | 0.2
Copy Room | 0.5
Classroom | 0.7 | Specialized Task | 0.4
Gym/Exercise Center | 0.5
Library Reading Area | 0.8 | Decorative/Display | 0.25
Library Stacks | 1
Retail Merchandise Sales | 0.95 | Decorative | 0.35
Retail Merchandise Sales | 0.95 | Wall Display (≤10'6") | 9.5 W/ft
Grocery Sales | 1 | Decorative | 0.35
Grocery Sales | 1 | Wall Display (≤10'6") | 6.6 W/ft
Parking Garage - Parking Zone | 0.1 | First ATM/Ticket | 100 W
Parking Garage - Daylight Adapt | 1
Manufacturing - Low Bay | 0.6 | Detailed Task | 0.2
Manufacturing - High Bay | 0.65 | Detailed Task | 0.2
Manufacturing - Precision | 0.85 | Precision Work | 0.7
2025 UPDATES: | Some area LPDs updated; Corridor reduced from 0.70 to 0.40; Restroom increased to 0.65

## MF_Envelope_Summary
Title 24-2025 Prescriptive Requirements - Multifamily Buildings
ENVELOPE REQUIREMENTS (SELECTED CLIMATE ZONES)
Component | Type | Metric | CZ1 | CZ3 | CZ6 | CZ9 | CZ12 | CZ16
Roof/Ceiling | Wood Frame | Max U-factor | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024
Exterior Walls | Wood Frame | Max U-factor | 0.065 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048
Exterior Walls | Steel Frame | Max U-factor | 0.084 | 0.071 | 0.071 | 0.071 | 0.071 | 0.071
Fenestration | All Other Windows | Max U-factor | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Fenestration | All Other Windows | Max RSHGC | NR | 0.23 | 0.23 | 0.23 | 0.23 | NR
Fenestration | Curtainwall/Storefront | Max U-factor | 0.38 | 0.41 | 0.41 | 0.41 | 0.41 | 0.38
Fenestration |  | Max WWR | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Entry Doors | Dwelling Unit | Max U-factor | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Entry Doors | Common - Swinging | Max U-factor | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Entry Doors | Common - Non-Swing | Max U-factor | 0.5 | 1.45 | 1.45 | 1.45 | 1.45 | 0.5

## Climate_Zones_Info
California Title 24 Climate Zones
Climate Zone | Representative City | General Characteristics
1 | Arcata | Cool coastal - Heating dominated
2 | Santa Rosa | Moderate coastal - Heating dominated
3 | Oakland | Bay Area coastal - Heating dominated
4 | San Jose-Reid | Bay Area - Moderate heating/cooling
5 | Santa Maria | Central coast - Moderate heating
6 | Los Angeles | South coastal - Moderate conditions
7 | San Diego | San Diego coastal - Mild year-round
8 | El Toro | Inland valleys - Moderate heating/cooling
9 | Burbank-Glendale | Inland valleys - Cooling dominated
10 | Riverside | Desert transition - Hot summers
11 | Red Bluff | North central valley - Hot summers
12 | Sacramento | Central valley - Hot dry summers
13 | Fresno | South central valley - Very hot summers
14 | China Lake | High desert - Hot dry, cold winters
15 | Palm Springs-Blythe | Low desert - Very hot summers
16 | Mt. Shasta | Mountain - Cold winters, moderate summers

## 2022_vs_2025_Changes
Title 24: Key Changes from 2022 to 2025
Category | Component | 2022 Requirement | 2025 Requirement | Impact
ENVELOPE | Metal Building Roofs | 0.041 U-factor | 0.038 U-factor | Stricter - 7% improvement
ENVELOPE | Wood Frame Roofs (CZ 6-8) | 0.034 U-factor | 0.047 U-factor | Relaxed for moderate zones
ENVELOPE | Various Wall Types | Varied by type | Generally improved | Multiple improvements
ENVELOPE | Fenestration | Various by type | Largely unchanged | Minimal changes
HVAC | Heat Pump Efficiencies | Specific EER/COP values | Federal Minimum references | Auto-updates with federal standards
HVAC | VRF < 65k Btu/h Cooling | 13.0 SEER | SEER2 after 1/1/2023 | New rating methodology
HVAC | VRF < 65k Btu/h Heating | 7.7 HSPF | 7.5 HSPF2 after 1/1/2025 | New rating methodology
HVAC | Larger VRF Systems | Specific EER/IEER | Federal Min IEER | Simplified compliance
LIGHTING | Complete Building LPDs | Same as 2025 | Unchanged | No change
LIGHTING | Corridor Areas | 0.70 W/ft² | 0.40 W/ft² | Significant reduction - 43%
LIGHTING | Restrooms | 1.00 W/ft² | 0.65 W/ft² | Reduction - 35%
LIGHTING | Most Other Areas | Various | Minor adjustments | Small refinements
OVERALL | Compliance Approach | Prescriptive values | More federal references | Simplification & auto-update
OVERALL | Documentation | Static requirements | Dynamic federal refs | Keeps pace with standards

## Notes_References
Title 24-2025 Prescriptive Requirements
IMPORTANT NOTES AND REFERENCES
KEY ABBREVIATIONS
U-factor | Overall heat transfer coefficient (Btu/h·ft²·°F) - Lower is better
SHGC | Solar Heat Gain Coefficient - Lower blocks more heat
RSHGC | Relative Solar Heat Gain Coefficient (accounts for external shading)
VT | Visible Transmittance - Higher allows more daylight
WWR | Window-to-Wall Ratio
LPD | Lighting Power Density (Watts per square foot)
EER/EER2 | Energy Efficiency Ratio (Btu/h per Watt)
SEER/SEER2 | Seasonal Energy Efficiency Ratio (2=newer test procedure)
IEER | Integrated Energy Efficiency Ratio
COP | Coefficient of Performance (unitless)
HSPF/HSPF2 | Heating Seasonal Performance Factor (2=newer test procedure)
Federal Minimum | References current federal standards which auto-update
2025 KEY CHANGES & NOTES
Envelope Improvements | Many envelope components have stricter requirements, particularly in select climate zones
Federal References | Many HVAC efficiencies now reference "Federal Minimum" allowing automatic updates
Rating Transitions | Transition from SEER to SEER2 (1/1/2023) and HSPF to HSPF2 (1/1/2025)
Lighting Reductions | Some interior LPDs reduced (corridors, restrooms)
Climate Zone Specific | Requirements vary by California climate zone (1-16)
IMPORTANT COMPLIANCE NOTES
1. Prescriptive vs Performance | Buildings can comply either prescriptively (meet all requirements) or via performance approach
2. Mandatory Requirements | Some requirements are mandatory regardless of compliance method
3. Updated Standards | This workbook reflects 2025 standards; 2022 comparison sheet included
4. Federal Integration | Federal Minimum references mean values update with DOE standards
5. Trade-offs | Some methods allow trade-offs between components
REFERENCES
Title 24, Part 6 | California Energy Code - Building Energy Efficiency Standards
Document | CEC-400-2025-010-F (2025 Final Standards)
Effective Date | January 1, 2026
Website | www.energy.ca.gov/title24
BASELINE MODELING NOTES
For Energy Models | These prescriptive values establish minimum baselines for compliance modeling
Envelope Assemblies | Use overall U-factors, not just insulation R-values
HVAC Systems | Baseline equipment efficiencies shown are minimums; check federal updates
Lighting | LPD values are maximum allowances for baseline
Climate Data | Use appropriate TMY3 or CTZ2022 weather files for 2025 compliance
Federal Minimums | Where "Federal Minimum" referenced, verify current DOE standards